## Electrical
Electrical BOQ
BOQ NO. | WORK DESCRIPTION | UNIT | Qty
1 | LT PANEL
1 | Design, fabrication, supply, installation, testing & commissioning of LT Switchgear Panels as mentioned below strictly in conformity with IEC 61439 and construction shall be class of IP4X for Indoor and IP5X for outdoor.The cubicle shall be of CRCA sheet steel, duly powder coated with polyester for out door and epoxy polyester for indoor. The switchboard shall be extendable type. The ACB / MCCB / MPCB / MCB shall be approved make and of specified short circuit rating and suitable for breaker coordination. Suitable bus bars of high conductivity Copper strips and mounted on non- hygroscopic insulating supports shall be provided. All components shall be approved type of components of recommended makes. All Switchgear components of suitable capacity as mentioned in the single line diagram and in conformity with technical specifications. Fully TYPE Tested assembly. (FTTA). Panels should have bimetaic strips for cable connectivity. Contractor should supply the discrimination studies along with Fault level study &arch flash study before manufacturing panels. Source A & Source B shall be colour coded as per standard colour code requirements i.e.
All LV panels shall be of fully type tested design. MCCB<=200A shall be Adjustable thermal & Adjustable Magnetic type & MCCB=>250A shall be MP based LSIG type. All MCCB’s shall be Plug in type. MCCB <= 200A shall be Adjustable thermal & Adjustable Magnetic type & MCCB => 250A shall be MP based LSIG type with provision to disable Ground & Neutral protections. The switching of incoming & outgoing circuits up to & including 630 amps will be plugin type moulded case circuit breakers (MCCB) and 800 amps and above rating will be draw out type air circuit breakers (ACB). All ACB will be EDO
1.1 | LT panel-1 & 2 | Nos | 2
Incomer-1 Rating & Quantity
MCCB Rated 800A, 415VAC, 50Hz, 4 Pole, 35 kA - 1 Nos Mic processor Based Energy Release with O/C,S/C,E/F protections with the following
Metering & Indicating Panel for Incomers
1no. 96 mm sq Digital multipurpose Energy Meter having measurement of Volts, Amps, PF, F, W, Wh, VA, VAh, Var, Varh and THDi with RS485 port, Accuracy Cl 1.0 (Model EM6400NG+ Series) along with CT's or IEM3350 Meter
Three phase LED Type Indicating Lights, ON/OFF/TRIP indicating lights for Incoming
Busbar
Electrolytic high conductivity Copper three phase and neutral busbars / Cable rated at 630 amps, 4 pole fault level of 35 kA. at 415 volts. The neutral busbar is to be of 100% capacity
Outgoings Rating & Quantity, Specification
O/G MCCB Rated 630A, 415VAC, 50Hz, 4P - 3 Nos
1.2 | UPS OP panel | Nos | 2
Incomer-1 Rating & Quantity
MCCB Rated 800A, 415VAC, 50Hz, 4 Pole, 35 kA - 2 Nos Mic processor Based Energy Release with O/C,S/C,E/F protections with the following
Metering & Indicating Panel for Incomers
1no. 96 mm sq Digital multipurpose Energy Meter having measurement of Volts, Amps, PF, F, W, Wh, VA, VAh, Var, Varh and THDi with RS485 port, Accuracy Cl 1.0 (Model EM6400NG+ Series) along with CT's or IEM3350 Meter
Three phase LED Type Indicating Lights, ON/OFF/TRIP indicating lights for Incoming
Busbar
Electrolytic high conductivity copper three phase and neutral busbars / Cable rated at 630 amps, 4 pole fault level of 35 kA. at 415 volts. The neutral busbar is to be of 100% capacity
Outgoings Rating & Quantity, Specification
O/G MCB Rated 32A, 230VAC, 50Hz, 4P - 4 Nos
O/G MCB Rated 63A, 415VAC, 50Hz, 4P - 9 Nos
O/G MCB Rated 40A, 415VAC, 50Hz, 4P - 2 Nos
1.2 | CDU Panel 1 & 2 | Nos | 2
Incomer-1 Rating & Quantity
MCCB Rated 40A, 415VAC, 50Hz, 4 Pole, 25 kA - 1 Nos Therman Mgnetic Release with O/C,S/C,E/F protections with the following
Metering & Indicating Panel for Incomers
1no. 96 mm sq Digital multipurpose Energy Meter having measurement of Volts, Amps, PF, F, W, Wh, VA, VAh, Var, Varh and THDi with RS485 port, Accuracy Cl 1.0 (Model EM6400NG+ Series) along with CT's or IEM3350 Meter
Three phase LED Type Indicating Lights, ON/OFF/TRIP indicating lights for Incoming
Busbar
Electrolytic high conductivity copper three phase and neutral busbars / Cable rated at 40 amps, 4 pole fault level of 25 kA. at 415 volts. The neutral busbar is to be of 100% capacity
Outgoings Rating & Quantity, Specification
O/G MCB Rated 32A, 230VAC, 50Hz, 4P - 2 Nos
O/G MCB Rated 16A, 415VAC, 50Hz, 2P - 2 Nos
1.3 | Chiller Panel | Nos | 0 | Chiller scope
Incomer-1 Rating & Quantity
MCCB Rated 800A, 415VAC, 50Hz, 4 Pole, 35 kA - 1 Nos Mic processor Based Energy Release with O/C,S/C,E/F protections with the following
Metering & Indicating Panel for Incomers
1no. 96 mm sq Digital multipurpose Energy Meter having measurement of Volts, Amps, PF, F, W, Wh, VA, VAh, Var, Varh and THDi with RS485 port, Accuracy Cl 1.0 (Model EM6400NG+ Series) along with CT's or IEM3350 Meter
Three phase LED Type Indicating Lights, ON/OFF/TRIP indicating lights for Incoming
Busbar
Electrolytic high conductivity Copper three phase and neutral busbars / Cable rated at 630 amps, 4 pole fault level of 35 kA. at 415 volts. The neutral busbar is to be of 100% capacity
Outgoings Rating & Quantity, Specification
O/G MCCB Rated 630A, 415VAC, 50Hz, 4P - 3 Nos(2 chiller, 1 spare)
O/G MCCB Rated 315A, 415VAC, 50Hz, 4P - 2 Nos (pump - 1, spare)
1.3 | ATS
Supply installation testing & commisioning of ATS with enclosure of the follwing sizes
| 32A 4P ATS with enclosure for CDU | Nos | 1
| 16A DP ATS with enclosure for Valve | Nos | 2
1.4 | Supply installation testing commisioning of 630A 4P 35kA MCCB in existing panel | Nos | 1
2 | IEC sockets
Supply installation, testing and commisioning of IEC 60309 sockets with enclosure with necessary supports as follows
2.1 | IEC 60309-32A,3P+N+E Interlocked type Socket with necessary enclosure |  | 6
2.2 | IEC 60309-63A,3P+N+E Interlocked type Socket with necessary enclosure |  | 16
2 | LT CABLES & TERMINATION
2.1 | Supply, testing and commissioning of following XLPE insulated, FRLS PVC outer sheathed Copper /Alluminium conductor Power cables (1100V grade) and installation in form of Horizontal and vertical laying of XLPE insulated Flexible/Armoured cables of below mentioned sizes in cable trays,hume pipe,cable shaft supported on structure/pull through pipes dewatering if required using own pumps, including pipes, supply and fixing of Aluminium strip number tags, supply and fixing of GI saddles and saddle bars, etc. including transportation from stores to site. Unpacking, with all labour and material as per specification of this tender and directions of Engineer-in-Charge.The cost shall includes all necessary supports.
a | 4C x 150 Sq.mm - Alm. Arm.Xlpe | RM | 110 | Earlier 160 mtrs
b | 1C x 150 Sq.mm - cu flexible | RM | 420
c | 4C x 150 Sq.mm - cu ARM | RM | 0 | Chiller cable
d | 1C x 95 Sq.mm - cu flexible | RM | 0 | Pump Cable
e | 4c x 10 x sqmm - cu flexible | RM | 40
f | 3c x 4 x sqmm - cu flexible | RM | 40
g | 5C x 16 Sq.mm - cu flexible | RM | 320
2.2 | Supply, Unloading, Handling, Shifting, Installation, Testing at site, Commissioning & Handing Over of Double Compression Nickel Plated Cable Glands & Cable terminations (Tinned Copper / Aluminium Lugs ) for XLPE/PVC insulated, FRLS PVC outer sheathed 1100 V, Copper conductor, unarmoured power cables including stripping of cable insulation, Drilling of gland plate, Clamping of cable cones, Ferrules etc.complete as per technical specifications, drawings, relevant standards and site conditions.The cost shall includes all necessary supports. Note: 1) Wherever the Aluminium cables are terminated on Copper Bus or visa versa, suitable size bimetalic washer shall be used. 2) Rate Quoted shall include the cost of Bimetalic washer.
a | 4C x 150 Sq.mm - Alm. Arm.Xlpe | NOS | 8 | Earlier 12
b | 1C x 150 Sq.mm - cu flexible | NOS | 34
c | 4C x 150 Sq.mm - cu ARM | NOS | 0 | Chiller cable
d | 1C x 95 Sq.mm - cu flexible | NOS | 0 | Pump Cable
e | 4c x 10 x sqmm - cu flexible | NOS | 32
f | 3c x 4 x sqmm - cu flexible | NOS | 4
g | 5C x 16 Sq.mm - cu flexible | NOS | 32
3 | CABLE TRAYS
3.1 | Design, Fabrication, Supply, Unloading, Handling, Installation, Commissioning & Handing Over of cable trays of following sizes, suspended from ceiling or fixed vertically on wall / column as per route directed at site, as approved complete as per technical specifications, drawings & relevant standards & site conditions. Tray shall be made out of 2 mm thick sheet.
Note: 1) Rate Quoted shall include cold galvanizing paint on welded spots. 2) Rate Quoted shall include site fabrication of required Bends, T-Junction, Elbows, X-Junction, Z-Sections, Reducer etc.
a | 300X100 mm wide HDG ladder tray | RM | 0 | For chiller cable
b | 300X100 mm wide Powder coated Perforated tray | RM | 60
c | 450X100 mm wide Powder coated Perforated tray | RM | 40
4 | EARTH FLAT
4.1 | Supply, Unloading, Handling, Installation, Testing & Commissioing of the following earthing strip along the cable trenches or cable trays or fixing to walls (by using proper size of spacer and saddles) or structures or buried individually in paved /unpaved areas ( minor civil work like chipping of paved surface finishing after laying grounding loop, etc. Welding at joints, providing anti-corrosive paint for welded portion, clamping & necessary hardware for connection, excavation & refilling, etc Including provision for risers at places as per approved drawings, all labour to be considered in installation work) & all other required materials complete as per drawings, specifications of this tender & directions of site in-charge. including earthing Clamps, terminal lugs etc.
a | 32 x 6 mm thick GI Strip | RM | 30
b | 25 x 6 mm thick GI Strip | RM | 0
e | 25 x 3 mm thick Cu Strip | RM | 20
f | 1C 6 Sqmm Cu Cable | RM | 30
g | 1C 25 Sqmm Cu Cable | RM | 30
h | 1c 95 Sqmm Cu cable | RM | 0 | For chiller earthing
Remarks
Earth pit not considered in scope
Earth pit to Data hall Earthing will be in customer scope
UPS considered for IT and CDU only

## Sheet1
IT Distribution
Sl.no | Load description | Load/Density | Qty | Total Load
1 | High density rack | 155 | 2 | 310 | kW
2 | Network racks | 14 | 3 | 42 | kW
3 | MCDU | 7 | 1 | 7 | kW
4 | Motorised Valves | 0.3 | 2 | 0.6 | kW
|  |  | Total demand for IT UPS | 359.6 | kW
|  |  | Proposed UPS capacity | 400 | kW | 89.9%
|  |  | Adding UPS Losses 3% | 370.388 | kW
|  |  | Battery Charging load | 16.2086 |  |  | Voltage | Power factor | Percentage of Overcurrent as per NEC | Total Breaker rating to consider | Considered
|  |  | Total load | 386.5966 | kW |  | 415 | 0.9 | 125% | 747.0155 | 800 A
Non IT distribution
Sl.no | Load description | Load/Density | Qty | Total Load
1 | Chiller | 240 | 1 | 240 | 1w+1s
2 | Pump | 115 | 1 | 115 | 1w+1s
| Prposed UPS capacity |  |  | 150 |  | 76.67%
| Adding UPS Losses 3% |  |  | 118.45 | kW
| Battery Charging load |  |  | 5.4029 | kW
| Total Load |  |  | 363.8529 | kW |  | 415 | 0.9 | 125% | 703.068 | 800 A